## Slide 1: UNIT-III TRANSFORMERS

## Slide 2: DEFINITION
Electrical Power transformer is a static device which transforms electrical energy from one circuit to another without any direct electrical connection and with the help of mutual induction between two windings. It transforms power from one circuit to another without changing its frequency but may be in different voltage level.

## Slide 3: Working Principle of Transformer
The working principle of transformer depends upon Faraday's law of electromagnetic induction. Actually, mutual induction between two or more winding is responsible for transformation action in an electrical transformer.
Faraday's Laws of Electromagnetic Induction :
According to these Faraday's laws, "Rate of change of flux linkage with respect to time is directly proportional to the induced EMF in a conductor or coil".

## Slide 4: Basic Theory of Transformer

## Slide 5
The alternating current through the winding (Primary) produces a continually changing flux or alternating flux that surrounds the winding.
If any other winding (secondary) is brought nearer to the previous one, obviously some portion of this flux will link with the second.
As this flux is continually changing in its amplitude and direction, there must be a change in flux linkage in the second winding or coil. According to Faraday's law of electromagnetic induction, there must be an EMF induced in the second.
If the circuit of the later winding is closed, there must be an current flowing through it. This is the simplest form of electrical power transformer and this is the most basic of working principle of transformer.

## Slide 6
So, Finally
A transformer is a device which transfers electrical energy (power) from one voltage level to another voltage level.
Unlike in rotating machines, there is no energy conversion.
A transformer is a static device and all currents and voltages are AC.
The transfer of energy takes place through the magnetic induction.

## Slide 7: Main Constructional Parts of Transformer
The three main parts of a transformer are given below:
Primary Winding of transformer - which produces magnetic flux when it is connected to electrical source.
Laminated Magnetic Core of transformer - the magnetic flux produced by the primary winding, that will pass through this low reluctance path linked with secondary winding and create a closed magnetic circuit.
Secondary Winding of transformer - the flux, produced by primary winding, passes through the core, will link with the secondary winding. This winding also wounds on the same core and gives the desired output of the transformer.

## Slide 8: Construction of the Core
The two most common and basic designs of transformer construction are the core type transformer and the Shell-type transformer.
In the “core” type (core form) transformer, the primary and secondary windings are wound outside and surround the core ring. In the “shell type” (shell form) transformer, the primary and secondary windings pass inside the steel magnetic circuit (core) which forms a shell around the windings as shown below.

## Slide 10
In the core type transformer construction, half of the primary and secondary windings are placed around each leg (or limb) of the transformers magnetic circuit as shown above to reduce the leakage flux. Here winding insulated by a part of core area.
In small size core type transformers, Rectangular core is used and for large size round/ cylindrical core is used.
Shell type transformer core involves the use of double magnetic circuit.
Both the windings are placed around the central limb, the other two limbs are acting simply as a low reluctance flux path. Here core is surrounded by winding.
The core type is generally more suitable for high voltage and small output, While the shell type is suitable for low voltage and high output.

## Slide 11: Types of Transformers Based on voltage step up & down

## Slide 12: EMF EQUATION
Let
N1 = Number of turns in primary windings.
N2 = Number of turns in second windings.
Φm= Maximum flux in core.
Φm = Bm*A
f = Frequency of A.C input in Hz
As shown in fig flux increases from its zero value to maximum value Øm in one quarter of the cycle i.e in ¼ second.
Average rate of change of flux = (Øm /(1/(4f) )= 4f Øm Wb/s or volt. i.e., Average e.m.f /per turn = 4f Øm volt.
If flux Øm varies sinusoidally, then r.m.s value of induced e.m.f is obtained by multiplying the average value with form factor.
Form factor =r.m.s value / Average value =1.11

## Slide 13
R.m.s value of e.m.f/turn = 1.11. 4 f Øm= 4.44f Øm volt
Now, r.m.s value of the induced e.m.f in the whole primary winding=( induced e.m.f/turn) *(number of primary turns)
E1 = 4.44fN1 Øm………………………………………(1)
E1 = 4.44fN1BmA. (Øm= BmA)
Similarly, r.m.s value of the e.m.f. induced in secondary is,
E2 = 4.44fN2 Øm
E2 = 4.44fN2BmA. (Øm= BmA)…………..(2)

## Slide 14
Transformation Ratio of Transformer(K):
This constant ‘k’ is called transformation ratio of transformer, if N2>N1, K > 1, then the transformer is step up transformer. If N2 < N1, K < 1, then the transformer is step down transformer.
K = E2/E1=N2/N1=I1/I2

## Slide 15: Ideal Transformer
Definition: An ideal transformer is an imaginary transformer which does not have any loss in it, means no core losses, copper losses and any other losses in transformer. Efficiency of this transformer is considered as 100%.
Ideal transformer model is developed by considering the windings of the transformer are purely inductive, the core of transformer is loss free and there is zero leakage reactance of transformer.

## Slide 16
Now if an alternating source voltage V1 is applied in the primary winding of that ideal transformer, there will be a counter self emf E1 induced in the primary winding which is purely 180° in phase opposition with supply voltage V1.

## Slide 17: Practical Transformer
Iron or core losses in magnetic core of transformer
Cu losses due to winding resistance
Leakage flux giving rise to leakage reactance

## Slide 18
Practical Transformer on No-Load:
The primary input current is not wholly reactive. The primary input current under no-load conditions has to supply
(i) iron losses in the core i.e. hysteresis loss and eddy current loss and
(ii) A very small amount of copper loss in primary (there being no Cu loss in secondary as it is open). Hence, the no-load primary input current I0 is not at 90° behind V1 but lags it by an angle φ0 < 90°.

## Slide 19
No Load input Power (W0)= V1I0Cosφ0
where cos φ0 is primary power factor under no-load conditions. primary current I0 has two components :
One in phase with V 1. This is known as active or working or iron loss component Iw , which supplies the core losses (eddy current and hysteresis).
Other component is in quadrature with v1 and is known as magnetizing (or) Reactive component Iμ which sets up the magnetic flux.

## Slide 20
The following points should be noted carefully :
The no-load primary current I0 is very small as compared to the full-load primary current (It is about 1 per cent of the full-load current). Hence Cu loss is negligibly small which means that no-load primary input power is practically equal to the iron loss in the transformer.

## Slide 21
Practical Transformer on Load:
When the secondary is loaded, the secondary current I2 is set up. The V1 magnitude and phase of I2 with respect to V2 is determined by the characteristics of the load. Current I2 is in phase with V2 if load is non-inductive, it lags if load is inductive and it leads if load is capacitive.
The secondary current sets up its own m.m.f= N2I2 and hence its own flux Φ2 which is in opposition to the main primary flux Φ which due to I0. The secondary ampere-turns N2I2 are known as demagnetizing amp-turns.

## Slide 22
The opposing secondary flux Φ2 weakens primary flux Φ momentarily, hence primary back e.m.f E1 tends to be reduced. Let the additional primary current be I2’. It is known as load component of primary current.
This current is anti phase with I2.The additional primary m.m.f N1 I2’ sets up its own flux Φ2’ which is in opposition to Φ2(but is in the same direction as Φ) and is equal to it in magnitude. Hence, the two cancel each other out.
So, we find that the magnetic effects of secondary current I2 are immediately neutralized by the additional primary current I2’ which is brought into existence exactly at the same instant as I2.

## Slide 24: Transformer with Resistive Winding, but No Magnetic Leakage
An ideal transformer was supposed to possess no resistance, but in an actual transformer, there is always present some resistance of the primary and secondary windings. Due to this resistance, there is some voltage drop in the two windings. The result is that :
(i) The secondary terminal voltage V2 is vectorialy less than the secondary induced e.m.f E2 by an amount I2R2 where R2 is the resistance of the secondary winding. Hence, V2 is equal to the vector difference of E2 and resistive voltage drop I2 R2.

## Slide 25
The vector diagrams for non-inductive, inductive and capacitive loads are shown in Fig (a), (b) and (c) respectively.

## Slide 26: Transformer With Resistive Winding and with Magnetic Leakage

## Slide 27
The vector diagram for such a transformer for different kinds of loads is shown in Fig above.
In these diagrams, vectors for resistive drops are drawn parallel to current vectors whereas reactive drops are perpendicular to the current vectors. The angle Φ1 between V 1 and I1 gives the power factor angle of the transformer.
It may be noted that leakage reactance can also be transferred from one winding to the other in the same way as resistance.

## Slide 28: Equivalent Resistance
In Fig above a transformer is shown whose primary and secondary windings have resistances of R1 and R2 respectively.
The resistances of the two windings can be transferred to any one of the two windings. The advantage of concentrating both the resistances in one winding is that it makes calculations very simple and easy. It will be proved that a resistance of R2 in secondary is equivalent to R2/K2 the equivalent secondary resistance as referred to primary.
The copper loss in secondary is I2R2. This loss is supplied by primary which takes a current of I1.
Hence if R2‘ is the equivalent resistance in primary which would have caused the same loss as R2 in secondary

## Slide 30
Note : It is important to remember that
(a) when shifting any primary resistance to the secondary, multiply by K22 i.e. (transformation ratio).
(b) when shifting secondary resistance to the primary, divide it by K22 .
(c) However, when shifting any voltage from one winding to another only K is used.
If referred to primary: V2/= V2/k
If referred to secondary: V1/= V1*k
(d) when shifting any current from one winding to another only K is used.
If referred to primary: I2/= I2*k
If referred to secondary: I1/= I1/k

## Slide 31: Leakage Reactance
Similar to the resistance:
Equivalent primary reactance referred to secondary:
X2/= X2/k2
Equivalent secondary reactance referred to primary:
X1/= X 1* k2
Total reactance referred to secondary winding:
X02= X2+X1/ i.e., X02= X2+ X1*k2
Total reactance referred to primary winding:
X01= X1+X2/ i.e., X01= X1+ X2/k2

## Slide 32: Transformer With Resistance and Leakage Reactance
In Fig below the primary and secondary windings of a transformer with reactance taken out of the windings are shown. The primary impedance is given by
Similarly Impedance Z2/= Z2/k2
Z1/= Z1* k2
Z02= Z2+Z1/ i.e., Z02= Z2+ Z1*k2
Z01= Z1+Z2/ i.e., Z01= Z1+ Z2/k2

## Slide 34
Example 32.15. A 30 kVA , 2400/120-V, 50-Hz transformer has a high voltage winding resistance of 0.1W and a leakage reactance of 0.22W. The low voltage winding resistance is 0.035 W and the leakage reactance is 0.012 W. Find the equivalent winding resistance, reactance and impedance referred to the (i)high voltage side and (ii) the low-voltage side.

## Slide 35: Equivalent Circuit
In a practical transformer -
Some leakage flux is present at both primary and secondary sides. This leakage gives rise to leakage reactance at both sides, which are denoted as X1 and X2 respectively.
(b) Both the primary and secondary winding possesses resistance, denoted as R1 and R2 respectively. These resistances causes voltage drop as, I1R1 and I2R2 and also copper loss I12R1 and I22R2.
(c) Permeability of the core can not be infinite, hence some magnetizing current is needed. Mutual flux also causes core loss in iron parts of the transformer.
We need to consider all the above things to derive equivalent circuit of a transformer.

## Slide 36
The no load current I0 is divided into, pure inductance X0 (taking magnetizing components Iμ) and non induction resistance R0 (taking working component Iw) which are connected into parallel across the primary. The value of E1 can be obtained by subtracting I1Z1 from V1. The value of R0 and X0 can be calculated as, R0 = E1 / Iw and X0 = E1/Iμ.
But, using this equivalent circuit does not simplifies the calculations. To make calculations simpler, it is preferable to transfer current, voltage and impedance either to primary side or to the secondary side.

## Slide 37
The figure below shows the equivalent circuit of transformer with secondary parameters referred to the primary.

## Slide 38
Now, let R1 + R2' = R01 and X1 + X2' = X01 Then the equivalent circuit of transformer becomes as shown in the fig below

## Slide 39
****Why Transformer Rating in kVA ?
Cu loss of a transformer depends on current and iron loss on voltage. Hence, total transformer loss depends on volt-ampere (VA) and not on phase angle between voltage and current i.e. it is independent of load power factor. That is why rating of transformers is in kVA and not in kW.

## Slide 40: Voltage Regulation
The voltage regulation is the percentage of voltage difference between no load (0V2) and full load voltages(V2) of a transformer with respect to its no load or full load voltage.
%Reg up= (0V2-V2)/V2* 100 or
%Reg down= (0V2-V2)/0V2* 100
Voltage regulation of transformer at lagging power factor
Voltage regulation of transformer at leading power factor

## Slide 41: Efficiency
%η = (Output/ Input ) * 100
%η = ( Vi cosφ / Vi cosφ +W i+W cu)*100
η at any load ‘x’ is defined as
%η = ( x*Vi cosφ / x*Vi cosφ+Wi+x2*W cu)*100
Condition for maximum efficiency is core losses= copper losses